## COVER
FABRICATION OF A CERTIFIED TURNKEY ANIMAL BIOSAFETY LEVEL-3 MODULAR LABORATORY
FOR KCCR
AT KUMASI ASHANTI REGION, GHANA
BILL OF QUANTITIES
(SECTION IX - LOT 1 MAIN WORKS)
Tenderer:

## BoQ ABSL MODULAR LABORATORY
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
1 |  | PRELIMINARIES AND GENERAL CONDITIONS
Description of Site
1.1 |  | The site is situated at Kumasi Centre for Collaborative Research in Tropical Medicine (KCCR), in Kwame Nkrumah University of Science and Technology (KUNST), GHANA
Description of the Works
The works comprise of:
1.2 |  | Fabrication of a Certified Animal Biosafety Level - 3 Modular Laboratory
The Contractor is to Design, Supply, Install, Assemble,
Test, and Commission a "Turnkey ABSL Modular
Laboratory" in accordance with the technical
specifications, drawings and requirements included in the
Tender Documents
Names of Parties
1.3 |  | The names of parties referred to in these
Bills of Quantities and in the Conditions of
Contract are as follows:
Employer: KCCR
Drawings used for Preparation of Bills of
Quantities
1.4 |  | Drawings of the General layout used for the preparation of this Bill of Quantities have been provided in the Section - X of the Tender document.
Specification
The whole of the Works are to be executed generally in
1.5 |  | In accordance with the "Technical Specifications and
Applicable standards and regulations are stated in
the Tender document and this Bills of Quantities.
Obscurities
Should there be any doubt or obscurity as to the meaning of
1.6 |  | any portion of the bills of quantities, the Tenderer shall
send an email of such doubt or obscurity as
possible in order that the doubt or obscurity may be
removed prior to the submission of his tender.
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Bills of Quantities
1.7 |  | The Tenderer shall not alter these Bills of Quantites
A price or rate shall be entered against each item in these
Bills of Quantities "Except for the HVAC system section, where the Tenderer shall provide quantities based on their proposed design concept."
Any item not priced shall be deemed to be allowed in
other prices or rates in these bills. The prices or rates
inserted shall be the fully inclusive value of the work
described under the several items including all costs and
expenses which shall be required in and for the
execution of the work described.
The Contractor shall submit his priced Bills of Quantities
for examination prior to the signing of the Contract.
Alternatives etc to the Contract Documents
Any alteration, amendment, addition to or deletion from the
printed text of these Contract Documents or the Form of
1.8 |  | Tender by the Tenderer/Contractor without the express
authorization of the Employer will be invalid and not
recognised or taken into account in interpreting the
obligations and requirements of the Contract Documents.
Pricing Bills of Quantities
The pricing of these Bills of Quantities shall be in Euro
currency (€). Should the priced Bills of Quantities of the
1.9 |  | Tender considered for acceptance show any correction
or alteration must be initialed by the Tenderer. Should the
priced Bills of Quantities of the Tender be considered
for acceptance, the submitted document shall form
part of the Contract.
All prices (unit price) shall be stated without tax (turnover tax, value added tax, or alike). The amount of applicable tax shall be based on the national valid tax rates and shall be added as the last item on the summary sheet of the Tender or BoQ
Item | Product Description | Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Shelter, Accomodation and Subsistence
1.1 |  | Accommodation for the Contractor's supervisory and engineering staff shall be provided by the Employer. Accordingly, the cost of such accommodation shall not be factored in the unit price.
Clearing from Tema Port
1.11 |  | The "Employer" shall be responsible for clearing all exported ABSL goods at the designated port of entry, including payment of applicable import duties, taxes, customs charges, and port handling fees.
Employer's On-site Technical Assistance
1.12 |  | The employer shall nominate a local technical assistant by making a technician available during the on-site assembly of the components for a defined period. The scope, availability, and working hours for the Employer-nominated technician must be clearly defined.
In a case where the Tenderer will require a local technician during the on-site assembly of the component, the Tenderer must propose the required technician qualifications and estimated hours for the Employer’s approval and provision. This ensures the provided assistance is relevant and competent.
Contractor remains responsible for specialist supervision and execution. Define scope, availability and working hours.
Setting Out and Civil Works
1.13 |  | The Employer shall be responsible for all primary civil works associated with the foundation and structural base of the ABSL facility, including substructure works, as shown in the drawings. The Tenderer shall review the provided civil and structural information and shall explicitly identify, in their Tender submission, any additional civil works required to accommodate their proposed design, equipment, or systems.
Temporary Storage
1.14 |  | The Employer shall ensure that all exported goods delivered
to site are properly received, securely stored, and adequately
protected gainst damage, theft, moisture, dust, a and adverse
environmental conditions
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Design Deliverables
1.15 |  | Drawings of the general layout are provided in Section IX in the Tender Document. Tenderers must submit a complete design package for the HVAC system comprising a detailed breakdown of all major components (AHUs, HEPA filters, dampers, ductwork, BIBOs, etc.) with specified models, capacities, and performance data. "The design must demonstrate compliance with the pressure control requirements of -150 Pa to +150 Pa for individual rooms". The Tenderer shall also submit a detailed structural design and an electrical diagram, including schematics, calculations, cable and load lists, component specifications, and installation details. |  | Item
Training of Operational Staff
1.16 |  | The Contractor shall provide on-site training for the Client’s technical and operational staff covering system operation, routine maintenance, safety procedures, troubleshooting, emergency response and BMS interface as well as submission of training materials. |  | Item
Operation and Maintenance Manual
1.17 |  | The Contractor shall submit a complete Operation & Maintenance (O&M) manuals, as-built drawings, equipment datasheets and manufacturer certifications, wiring diagrams, control schematics, testing and commissioning reports, and warranty certificates |  | Item
Spare Parts and Warranty Support
1.18 |  | The Contractor shall supply a sufficient quantity of critical spare parts for a minimum of 12 months of operation, including pre and secondary filters, control fuses and sensors, gaskets and sealing materials for containment systems |  | Item
Works Programme and Progress Charts
The Contractor shall submit a detailed and realistic
1.19 |  | Works Programme and charts as specified in the |  | Item
Tender Invitation Section under "clause 10" having
regard to the damages of delays before the
commencement of the Works.
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Labour, Tools, Plants and Equipment
1.2 |  | The Tenderer shall provide all labour, tools, lifting equipment, testing instruments, PPE, and consumables required for the installation, on-site assembling, testing, and commissioning of the ABSL-3 Laboratory, unless specifically stated otherwise. |  | Item
Logistical Methodologies
1.21 |  | The Contractor shall be responsible for all costs and arrangements relating to the export of the goods from the country of origin up to the designated port of entry. This shall include, but not be limited to, export documentation, export duties (if any), inland transportation to the port of shipment, loading charges, ocean/air freight, marine insurance, and any other related logistical expenses. |  | Item
Tenderer must provide a logistical methodology statement outlining the proposed shipping route, Incoterms (e.g., CIF Tema), transport timelines, and risk mitigation strategies for the sensitive modular and HVAC components.
The Tenderer must not include import duties and levies of the goods into this cost item.
Progress Photographs
1.22 |  | The Contractor shall submit detailed weekly progress reports of the works. The report shall include, but not be limited to, the Executive summary of activities carried out during the reporting period., updated work programme indicating planned versus actual progress, and percentage completion of each major work item in the BoQ. Photographic documentation clearly showing progress of all ongoing works, status of procurement and delivery, Quality control activities undertaken, testing, and compliance with ABSL-2 standards. Health, safety, incidents, and mitigation measures (if any), key personnel on site, identified challenges, delays, or risks affecting progress, with proposed corrective actions, and planned activities for the subsequent week. |  | Item
First Aid Equipment
|  | The Contractor shall provide adequate first aid equipment |  | Item
1.23 |  | which shall be available for the use of the workmen during
working hours.
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
COLLECTIONS
|  | Total brought down from page No. ABSL-3/4 |  |  |  | 0
|  | Total brought down from page No. ABSL-3/5 |  |  |  | 0
TOTAL 1 - PRELIMINARIES
|  | Carried to Summary |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
2 |  | MODULAR UNIT/STRUCTURAL WORKS
Modules Units shall be non-combustible, fire-resistant, moisture-resistant, and suitable for laboratory use, and shall be installed on approved galvanized steel framing complete with all fixings, joint treatments, sealing, and finishing.
The entire modular envelope, including all panel joints, interfaces, and service penetrations, shall be properly sealed to achieve a maximum air leakage rate of less than 0.5% of the total room volume at 250 Pa, to support the HVAC pressure control regime.
2.1 | Wall Panels | Supply and install "50mm thick handmade magnesium oxysulfide (MgO) wall panel" or "approved equivalent" comprising double-sided 5mm thick face boards with a core density of not less than 900 kg/m³ and not exceeding 1,200 kg/m³ as exterior and interior wall partition panels at 3.00m high. "Quantity includes Length and Height of the entire layout" | 130 | m² |  | 0
2.2 | Ceiling Panels | Supply and install 50mm thick handmade magnesium oxysulfide (MgO) ceiling panel or "approved equivalent"comprising double-sided 5mm thick MgO face boards with a core density of not less than 900 kg/m³ and not exceeding 1,200 kg/m³. | 60 | m² |  | 0
2.3 | Structural Framing | Supply, fabrication and installation of a galvanized steel framing system comprising cold-rolled galvanized steel studs and tracks with a minimum zinc coating of Z275 (275 g/m²) and minimum base metal thickness of 0.9 mm, fixed at appropriate centers, complete with all anchors, connectors, bracing, and accessories, to support wall panels at a "net indoor height 3.0m high" | 60 | m² |  | 0
2.4 | Structural Framing for HVAC Duct and Piping insulation | Supply, fabricate, and install a modular container service zone (technical room) comprising a galvanized steel framing system and magnesium oxysulfide wall panels, designed with adequate clear internal height to accommodate all ductwork, piping, insulations, and electrical distribution boards |  | ls
2.5 | Outer Frame | Supply and installation of outer wall protection framing, including a roof structure securely fixed to the primary modular structure to form a continuous protective frame to external walls and ceiling, including all necessary accessories. Ensure airtightness and watertightness. The complete modular envelope, including all panel joints and penetrations, must be sealed to achieve a maximum leakage rate (e.g., < 0.5% of total volume at 250 Pa) to support the HVAC pressure control regime. | 100 | m² |  | 0
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Con't Modular Unit/Structure Works
2.6 | Flooring | Supply and install "2.5/3.0 mm thick homogeneous, static-dissipative vinyl flooring" of approved color, fully bonded with approved adhesive, heat-welded joints, abrasion and chemical resistant, complete with a) 100 mm high integral coved skirting, trims, sealants, surface preparation, and all accessories, suitable for ABSL-3 laboratory environment. | 60 | m² |  | 0
|  | To Collection |  |  |  | 0
COLLECTIONS
|  | Total brought down from page No. ABSL-3/7 |  |  |  | 0
|  | Total brought down from page No. ABSL-3/8 |  |  |  | 0
Total 2- MODULAR UNIT/STRUCTURAL WORKS
|  | Carried to Summary |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
3 |  | DOORS AND WINDOWS
Doors shall be interlocked to prevent the simultaneous opening of adjacent doors within the same airlock and shall be equipped with access control systems. The door interlock system shall be integrated with the room pressure monitoring system. In the event that a room falls outside its designated pressure range, an audible and/or visual alarm shall be triggered. Door hardware shall be designed and rated to operate effectively against a minimum pressure differential of 150 Pa and must be Zero Leak.
"Door profile shall be submitted to the Employer for approval before installation."
3.1 | Single door I | Supply and install a single leaf door of size 1200 (W)x2100mm (H) high, including a 50mm thick frame with a)1.2mm thick galvanized plate surface material b) magnesium oxysulfide inside panel c) 368x586mm hollow tempered double glass view window, complete with all necessary accessories, including door lock and door closer hardware mechanisms. | 3 | Pcs |  | 0
3.2 | Single door II | Supply and install a single leaf door of size 800x2100mm high, including 50mm thick frame with a)1.2mm thick galvanized plate surface material, b) magnesium oxysulfide inside panel c) 368x586mm hollow tempered double glass view window, complete with all necessary accessories, including door locks, door closer hardware mechanisms. | 8 | Pcs |  | 0
3.3 | Side View glass window | Supply and install 6mm thick double glazing windows tempered glass with aluminum alloy window frame of a) Dimensions: 775mmx1600mm b) Frame Shape: L-shaped corner c) Frame color: Black | 1 | Pc |  | 0
3.4 | Exterior Window | Supply and install "zero-leak" 6mm thick double tempered glass window with aluminum alloy window frame of a) Dimensions: 300mm dia b) Shape: Round/L-shaped corner c) Frame color: Black/white, as per approved drawings | 3 | Pcs |  | 0
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Con't Doors and Windows
Passbox:
The passbox shall be constructed with gasketed, airtight doors and the interlock must ensure one door is fully closed and sealed before the other can be opened, preserving room pressure differentials.
"Product shall be submitted to the Employer for approval before installation."
3.5 | Static Passbox | Supply and install "Static pass box" of a) Inner size: 600x600x600mm b) Outer size:770x680x730 c)External/Internal: Stainless steel 304L, d) Electronic Interlock, airtight doors and integrated UV-C sterilization lamp with timer-controlled operation, as per specification. | 1 | Pc |  | 0
3.6 | Dynamic Passbox | Supply and install "Dynamic Pass Box" of a) Inner size: 600x600x600mm b) Outer size:780x680x1200mm c)SUS 304L Differential Pressure Gauge, d) Domestic Fan, double Layer Steel Screen Printing Glass, Inner Door, Electronic Interlock, Sterilization Lamp. | 2 | Pcs |  | 0
|  | To Collection |  |  |  | 0
COLLECTIONS
|  | Total brought down from page No. ABSL-3/9 |  |  |  | 0
|  | Total brought down from page No. ABSL-3/10 |  |  |  | 0
Total 3 - DOORS AND WINDOWS
|  | Carried to Summary |  |  |  | 0
Item | Product Description | Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
4 |  | HVAC SYSTEM
All Tenderers shall design, supply, install, test, commission, and hand over a complete HVAC system. The design must unequivocally demonstrate the capability to individually control and maintain the air pressure of each listed room as indicated in the layout to any set point within the range of "-150 Pa to +150 Pa" relative to adjacent areas. The system must be capable of dynamic control, responding to filter loading, door openings, and other disturbances to re-establish the set-point pressure within a defined time (e.g., within 30 seconds).
All Tenderers shall prepare and insert their own quantities based on their proposed HVAC system concept design. The quantities provided shall include all components, accessories, and ancillary works necessary to deliver a complete and functional HVAC system, including an integrated BMS system. The works as follows:
4.1 | Air Handling Unit | Supply and install a dedicated modular, double-skinned AHU 01) of a non-recirculating (100% fresh air) system with (G4) Primary Filters and (F7) Secondary classification effect Filters, and Redundancy (N+1) for supply fans. The AHU casing must be airtight to prevent leakage. |  | Unit |  | 0
4.2 | HEPA Filters | Supply and install high-efficiency particulate air (HEPA) filters rated at H13/H14 classification in accordance with EN 1822 standards and rated air volume of 500m3/h. Filters shall be capable of removing ≥99.99% (H13) or ≥99.99% (H14) of airborne particles ≥0.3 microns with initial resistance Pa: ≤ 230 and liquid sealed high efficiency. |  | Unit |  | 0
4.3 | Cooling System | Supply and install a complete centralised cooling system designed to provide efficient and reliable cooling for the Laboratory |  | Unit |  | 0
4.4 | Dampers | Supply and Installation of high-speed actuating control dampers for precise airflow regulation, and gas-tight isolation dampers for decontamination cycles. All dampers must be suitable for the system pressure (minimum 150 Pa) and include position feedback for the BMS. |  | Unit |  | 0
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Con't HVAC System
4.5 | Dampers | Supply and install motorized bubble-tight decontamination dampers for use within the HVAC system to a provide complete airtight isolation of duct sections during gaseous decontamination with a leak class of SMACNA Class 3 (0.1% leakage of rated flow at a pressure differential of 150 Pa). |  | Unit |  | 0
4.6 | Dampers | Supply and installation of volumetric (balancing) dampers within the HVAC ductwork system to regulate and balance airflow quantities to maintain required air changes per hour (ACH), directional airflow, and pressure differentials in containment areas |  | Unit |  | 0
4.7 | Ducting | Supply, fabricated and install ductwork constructed to "SMACNA or an approved local equivalent", designed to Class A (high-pressure) standards, complete with appropriate thermal and acoustic insulation, all joints sealed for the HVAC installation serving the laboratory. Ductwork shall be pressure and leak tested at 1.5 times the maximum operating pressure to ensure high airtightness and support the pressure control strategy. |  | Unit |  | 0
4.8 | Air Diffusers | Supply, install ceiling-mounted air diffusers complete with accessories for the HVAC system serving the laboratory to ensure uniform air distribution, proper air change rates, and maintenance of pressure differentials within containment areas. |  | Unit |  | 0
4.1 | BIBO | Supply and install a Bag-In/Bag-Out (BIBO) of H14 filter, housing system, complete with HEPA filter(s) for safe containment and replacement in the HVAC exhaust/supply system. The BIBO housing must be of welded construction and leak-tested to the same standard as the ductwork and shall allow contaminated filter removal without exposure to maintenance personnel or the environment. |  | Unit |  | 0
4.11 | Non Return Dampers | Supply and install non-return dampers (backdraft dampers) within the HVAC ductwork system. Dampers shall prevent reverse airflow, protect containment integrity, and maintain designed pressure differentials within laboratory spaces |  | Unit |  | 0
|  | To Collection |  |  |  | 0
Item | Product Description | Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Con't HVAC System
4.12 | Exhaust Fans | Supply and install "centrifugal axial or approved equal exhaust fans" with N+1 redundancy to maintain the required negative pressure within the laboratory at all times. The fan control system (via VFDs) must be integrated with the BMS to ensure the exhaust system can always maintain the required negative pressure, even with filter loading or a fan failure |  | Unit |  | 0
4.13 | Exhaust stack | Supply and install an exhaust stack from "stainless steel (Grade 304L/316L) or hot-dip galvanized steel" for safe and 100% discharge of laboratory exhaust air from the laboratory into the atmosphere to ensure proper dispersion of contaminated air, prevent backflow, and comply with local environmental and safety standards. |  | Unit |  | 0
4.14 | Integrated Room Decontamination System | Supply and install a complete system for whole-room gaseous decontamination," as Vaporized Hydrogen Peroxide generator and controls" capable of decontaminating all room surfaces, the interior of exhaust ductwork connected to the room, including injection and distribution points, a catalytic converter for aeration, and safety interlocks. |  | Unit |  | 0
4.15 | Building Management System (BMS) | Supply, install, and commission a "Direct Digital Control (DDC) system or approved equal" for comprehensive monitoring and control of the HVAC system with a graphical user interface displaying real-time pressure for each room, allow for individual set-point adjustment (-150 Pa to +150 Pa), record historical data, and provide audible and visual alarms for pressure deviations. |  | Unit |  | 0
4.16 | (Optional) Room Pressure Monitors | Supply and install a certified, touch-screen room pressure monitor for each containment room (Main Laboratory, Microscopy Room etc.) to display current pressure differential, set-point, alarm status, with audible and visual alarms that trigger when pressure deviates beyond a user-defined tolerance (e.g., ± 5 Pa). |  | Unit |  | 0
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
COLLECTIONS
|  | Total brought down from page No. ABSL-3/11 |  |  |  | 0
|  | Total brought down from page No. ABSL-3/12 |  |  |  | 0
|  | Total brought down from page No. ABSL-3/13 |  |  |  | 0
Total 4 - HVAC SYSTEM
|  | Carried to Summary |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
5 |  | ELECTRICAL SUPPLY/ POWER/ LIGHTING
The Tenderer shall design a schematic electrical diagram based on the provided layout, supply, install, test, and commission a complete electrical system for the ABSL modular laboratory. The design must include a dedicated and uninterruptible power supply (UPS) circuit for the BMS, pressure sensors, and all HVAC controls to ensure pressure monitoring and control is maintained during a power failure.
The works shall include all materials, accessories, containment, terminations, labeling of all DBs, testing, and commissioning of electrical system necessary to deliver a fully functional and safe system. Details as follows;
5.1 | Wiring | Supply and install a complete electrical wiring system for ABSL 3 modular laboratory, including copper cables, aluminium armoured/flexible cables, conduits, cable trays, earthing and bonding, emergency circuits, containment sealing and testing. |  | ls
5.2 | Distribution Board for lighting, Sockets, etc. | Supply and install 6-way Distribution Board, complete with 1Nos 125A MCB incomer, 32A Single Pole MCB outgoing, 20A single pole MCB outgoing, 16A Single Pole MCB outgoing, 10A single pole MCB outgoing, LCD, ELCB, copper busbars, internal wiring, earthing, labeling or "approved equal base on your proposed design" | 1 | Set |  | 0
5.3 | Distribution Board for HVAC & critical loads | Supply and Install 8-Way Wall Mount Power Distribution Board Complete with, 1 Nos 250A 4-Pole MCCB incomer, 2 Nos 125A Three Pole MCB outgoing, 2 Nos 100A Three Pole MCB outgoing, 2 Nos 63A Three Pole MCB outgoing, LCD , ELCB, copper busbars, internal wiring, earthing, clearly labelled, testing and commissioning. "approved equal base on your proposed design" | 1 | Set |  | 0
5.4 | Lighting | Supply and install a "35W 600x600mm Philips electronic or approved equivalent" cleanroom-rated LED lighting BSL lab compatible, 'O' leak with integrated emergency backup power capability of 60–90 minutes duration, fixed inside ceiling including all accessories. | 16 | Pcs |  | 0
5.5 | Sockets | Supply and installation of 13AMPS switch power socket with inner and outer plates complete and clearly labelled | 39 | Pcs |  | 0
|  | To Collection |  |  |  | 0
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
Con't Electrical Spply/Power/lighting
5.6 | Switch | Supply and installation of 6A flush switch complete and clearly labelled | 12 | Pcs |  | 0
5.7 | Surveillance system cameras | Supply and Installation of IP CCTV surveillance camera system (4MP minimum) complete with PoE, IR night vision, IP66 housing, NVR with 30-day storage, cabling, mounting accessories, testing and commissioning, suitable for ABSL laboratory environment. | 10 | Pcs |  | 0
|  | To Collection |  |  |  | 0
COLLECTIONS
|  | Total brought down from page No. ABSL-3/15 |  |  |  | 0
|  | Total brought down from page No. ABSL-3/16 |  |  |  | 0
Total 5 - ELECTRICAL SUPPLY/ POWER/ LIGHTING
|  | Carried to Summary |  |  |  | 0
Item | Product Description | Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
6 |  | PLUMBING/SANITARY/FUNITURE/EQUIPMENT
The Tenderer shall be responsible for the installation of the interior layout of the plumbing works only. All external water supply and waste pipework shall be executed by the Employer. All penetrations through the modular envelope and room partitions for plumbing pipes must be sealed airtight with approved fire-stopping and airtight sealants to maintain pressure differentials.
All Sanitary fittings/Equipment shall be original, of high quality and approved by the "Employer" before fixing
6.1 | Water supply system | Supply and install internal cold water distribution and sewage drainage pipework with a) 12mm diameter uPVC pipes connected to the sinks, autoclave machine, and the shower unit b) including all accessories complete and operational. |  | ls
6.2 | Shower | Supply and install a cleanroom shower cubicle size 800 × 800 mm, complete with all necessary fittings and accessories, securely fixed to modular panel walls within the laboratory structure | 1 | set |  | 0
6.3 | Stainless steel sink | Supply and install a stainless steel laboratory sink Grade 304L size 700 x 400mm(LxW), complete with all necessary fittings and accessories, securely fixed to modular panel walls within the modular laboratory structure | 1 | No |  | 0
6.4 | Stainless steel sink | Supply and install a stainless steel laboratory sink size 350 x 400mm(LxW), complete with all necessary fittings and accessories, securely fixed to modular panel walls within the modular laboratory structure | 1 | No |  | 0
6.5 | Water Pump | Supply "water booster pump with output range 0 -5Bar pressure", complete with all standard accessories, suitable for boosting laboratory water supply pressure | 1 | pc |  | 0
6.6 | Laboratory Bench | Supply and install a "stainless steel grade 304L" Laboratory Work Bench with a) worktop of minimum thickness 1.5mm, b)bench height 900mm c) bench width 600mm d) Length 2700mm, complete with all necessary supports, fixings, and accessories | 1 | set |  | 0
6.7 | Laboratory Bench | Supply and install a "stainless steel grade 304L"Laboratory Work Bench with a) worktop of minimum thickness 1.5mm, b)bench height 900mm c) bench width 600mm d) Length 1400mm, complete with all necessary supports, fixings, and accessories | 1 | set |  | 0
Total 6 - PLUMBING/SANITARY/FUNITURE/EQUIPMENT
|  | Carried to Summary |  |  |  | 0
Item | Product Description | Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
7 |  | DISINFECTION & DECONTAMINATION SYSTEMS
"Producst shall be submitted to the Employer for approval before installation."
7.1 | Wall UV disinfection lamp | Supply and installation ceiling mounted "surface disinfection lamp of UV 254 nm wavelength", with control panel, timer, safety interlock integration to enable door access control system to automatically turn off the UV lamps if a door is opened to preventing human exposure, warning indicators, mounting accessories, electrical connection, status monitoring on BMS, testing and commissioning in 1) main laboratory 2) necroscopy 3) sterile storage 4) cleaning and preparation room | 4 | Pcs |  | 0
7.2 | UV disinfection lamps for water tanks | Supply UV water disinfection system complete with UV lamp (minimum 40 mJ/cm² dose), quartz sleeve, control panel with alarms and intensity monitoring, isolation valves, bypass line, electrical connections, installation, testing, and commissioning for inlet and outlet water disinfection | 2 | Pcs |  | 0
7.3 | Filters | Supply a "Three-Stage Water Filtration System" Rated for minimum 10–20 L/min flow, 2–6 bar pressure Complete with housings, mounting brackets, and necessary fittings | 1 | set |  | 0
7.4 | Air Curtain | Supply and installation of "sensor-based wall or ceiling-mounted air curtain" complete with a) high-efficiency fan, b) automatic activation sensor, c) adjustable airflow control, d) corrosion-resistant, including all electrical connections, testing and commissioning at the ABSL laboratory door opening. | 3 | Pcs |  | 0
Total 7 - DISINFECTION & DECONTAMINATION SYSTEMS
|  | Carried to Summary |  |  |  | 0

## SUMMARY
Item | Product Description | Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
SUMMARY
1 |  | PRELIMINARIES AND GENERAL CONDITIONS | …..... | …..... | …..... | 0
2 |  | MODULAR STRUCTURAL WORKS | …..... | …..... | …..... | 0
3 |  | DOORS AND WINDOWS | …..... | …..... | …..... | 0
4 |  | HVAC SYSTEM | …..... | …..... | …..... | 0
5 |  | ELECTRICAL SUPPLY/ POWER/ LIGHTING | …..... | …..... | …..... | 0
6 |  | PLUMBING/SANITARY/FUNITURE/EQUIPMENT | …..... | …..... | …..... | 0
7 |  | DISINFECTION & DECONTAMINATION SYSTEMS | …..... | …..... | …..... | 0
|  | TOTAL OF WORKS | A |  |  | 0
ADD
|  | Price and Physical Contingencies | B=10% OF A |  | 10% | 0
|  | SUB TOTAL (ToW + CONTINGENCIES) | C=A+B |  |  | 0
ADD/SUBTRACT
|  | ADJUSTMENT ITEM/DISCOUNT | D
|  | FRABRICATION OF A CERTIFIED TURNKEY ABSL-3 MODULAR LABORATORY AT KCCR, GHANA | E=C-D |  |  | 0
CARRIED TO FORM OF TENDER
TO BE COMPLETED IN ……………………….. MONTHS
Signature:
For and on behalf of (Company Name and Address):
Contractor's Licence No:
Date: