## COVER
FABRICATION OF A CERTIFIED TURNKEY ANIMAL BIOSAFETY LEVEL-3 MODULAR LABORATORY
FOR KCCR
AT KUMASI ASHANTI REGION, GHANA
BILL OF QUANTITIES
(SECTION IX - LOT 2 BACKUP POWER SYSTEM)
Tenderer:

## BoQ BACKUP POWER SYSTEM
Item | Product | Description/Specification | Qty | Unit | Unit Price Euro (€) | Amount Euro (€)
8 |  | BACKUP POWER SUPPLY SYSTEM
Supply, install, test, and commission the following backup power supply systems for the ABSL 3 Laboratory:
8.1 | Backup Generator | 50kVA diesel generator set rated at 400/230V, 50Hz, 0.8 power factor, three-phase, 557 amps, complete with an Automatic Voltage Regulator (AVR) and Automatic Transfer Switch (ATS) to serve as a backup power supply for the ABSL laboratory in the event of the main power failure. | 1 | set |  | 0
8.2 | Backup Batteries | Industrial-grade, online double-conversion Uninterruptible Power Supply (UPS) system to provide conditioned and backup power to all critical loads as defined in the Critical Loads Schedule to bridge the power gap between mains failure and generator startup, ensuring no interruption to containment monitoring, BMS, access control, and critical safety systems. Refer to the attached Critical Loads Schedule for detailed specifications and connected items. | 1 | set |  | 0
8.3 | Maintenance changeover switch | Wall-mount automatic changeover switch, complete with mechanical interlocking to allow safe isolation and bypass of the UPS for servicing without interrupting power to critical loads. | 1 | set |  | 0
|  | Total 8 - BACKUP POWER SUPPLY SYSTEM |  |  |  | 0

## CRITICAL LOADS
Load Ref. | Description of Load / Instrument | Location / Room | Qty | Unit Power (W) | Total Power (W) | Priority | Remarks
CL-01 | Building Management System (BMS) Controller | Main Electrical Room | 1 | 500 | 500 | 1 | Central processor for all pressure, temp, and HVAC control.
CL-02 | BMS Remote I/O Modules | Throughout facility | 4 | 150 | 600 | 1 | Distributed control points for pressure sensors and damper actuators.
CL-03 | Room Pressure Monitors | Main Laboratory | 1 | 50 | 50 | 2 | Local display and alarm for pressure differential.
CL-04 | Room Pressure Monitors | Microscopy Room | 1 | 50 | 50 | 2 | Local display and alarm for pressure differential.
CL-05 | Room Pressure Monitors | Sterile Storage | 1 | 50 | 50 | 2 | Local display and alarm for pressure differential.
CL-06 | Room Pressure Monitors | Cleaning/Preparation Room | 1 | 50 | 50 | 2 | Local display and alarm for pressure differential.
CL-07 | Room Pressure Monitors | Necroscopy Room | 1 | 50 | 50 | 2 | Local display and alarm for pressure differential.
CL-08 | Access Control Panel | Main Entrance | 1 | 200 | 200 | 3 | Controls all door interlocks and card readers.
CL-09 | Door Interlock Controllers | At each airlock | 3 | 100 | 300 | 3 | Local logic controllers for door sequencing.
CL-10 | HVAC Damper Actuators (Control) | Throughout HVAC | 12 | 50 | 600 | 4 | Power to hold position or modulate.
CL-11 | VFD Control Circuits | AHU / Exhaust Fan rooms | 4 | 100 | 400 | 5 | Low-voltage controls for the fan VFDs.
CL-12 | Emergency Lighting Inverter | Containment suites | 1 | 1500 | 1500 | 6 | Provides immediate illumination for safe egress.
CL-13 | Critical Freezer (-80°C) – Controller | Main Laboratory | 2 | 300 | 600 | 7 | Controller and alarm system only (not compressor).
CL-14 | Incubator – Controller | Main Laboratory | 1 | 200 | 200 | 7 | Controller and alarm system only.
CL-15 | Data Logger / Server for Lab Data | Office / Server Rack | 1 | 400 | 400 | 8 | Records all critical environmental data.
CL-16 | Monitoring Computer (BMS Workstation) | Office / Control Room | 1 | 300 | 300 | 8 | HMI for operators.
CL-17 | Intercom / Communication System | Throughout facility | 1 | 300 | 300 | 9 | Allows internal communication during emergency.
CL-18 | Critical Power Outlets (Selected) | Main Laboratory | 4 | 500 | 2000 | 10 | For momentary equipment. Marked red.
CL-19 | Critical Power Outlets (Selected) | Microscopy Room | 2 | 500 | 1000 | 10 | For momentary equipment. Marked red.
CL-20 | UV Lamp Control Panels | Main Lab, Necroscopy | 4 | 50 | 200 | N/A | Control logic for UV interlocks.
|  | Total Wattage |  |  | 9350
Add
|  | 20% Safety Factor |  | 20% | 1870
RECOMMENDED UPS/BACK UP BATTERIES CAPACITY |  |  |  |  | 11220 | 14kVA